## Slide 1: IAQ Keeper – Indoor Air Quality Monitoring and Control System
Features
  Real-time Device Status and Alerts
    IAQ data
    Electrostatic Precipitator(ESP) and ESP Cleaner Status
    Air Handle Unit(AHU) Fan Status
    ESP Fault Alarms
  Rules Engine & Schedules
    Automatically runs at optimal settings based on predefined rules and actions
    Automatically turn on/off ESP and ESP Cleaner after desired amount of time
    Schedule by weekly, daily and/or hourly
  Reports
    Purification Time
    Energy Usage
    Difference between Outdoor AQI and Indoor AQI
    Device Alarms
  Forcing Control
  Historical Trend
  Collect public Outdoor AQI data
  Pure Web UI

## Slide 2: System Architecture
Field Controller
PM2.5 Sensor
AHU#2
Field Controller
PM2.5 Sensor
AHU#31
Field Controller
PM2.5 Sensor
AHU#1
RS485 Bus #1
...
Supervisory Controller
LAN/WLAN
RS485 Bus #2
RS485 Bus #6
Public Outdoor AQI
Zone #1
Zone #2
Zone #31

## Slide 3: Field Controller
Provides direct, closed loop control over mechanical refrigeration equipment
Either as a standalone device or as a part of a larger networked control system.
Protocol: Modbus/RTU
Built-in Logics (Non-Programmable)
  Desired PM2.5 Value: Should set expected value via Modbus which is in range 5~100ug/m³; Should persistent the value either Modbus is off line or power is off.
  Actual PM2.5 Value: Should be set to the value of PM2.5 sensor If the PM2.5 sensor is connected to A!1, else if the controller is connected to Modbus the value should be set to other sensor’s value via Modbus, else the value should be the latest value persisted. The actual value’s range is 5~300ug/m³.
  ESP Status（DO1）: When ESP Forcing Control Mode is OFF, If the actual PM2.5 value is higher than the sum of the desired value and the dead band value then ESP should ON, otherwise OFF. When ESP Forcing Control Mode is ON, ESP can be set ON/OFF via Modbus directly.
  ESP Cleaner Status（DO2）: When ESP Cleaner Forcing Control Mode is OFF, if AHU Fan is ON and ESP Cleaner is set to ON via Modbus, the ESP Cleaner is ON, otherwise OFF. When ESP Cleaner Forcing Control Mode is ON, ESP Cleaner can be set ON/OFF via Modbus directly.
RS485 BUS
PM2.5 Sensor
Modbus/RTU
AI(1-2)
DO(1-2)
DI(1-4)
PWR
DC12V
Masks
AHU
ESP

## Slide 4: Supervisory Controller Hardware
Provides integrated control, supervision and network management services to one or more field controllers.
Also provides system-wide coordination to automate operations, improve occupant comfort, reduce energy usage, and optimize operating efficiencies.
Specifications
  IPC-S2221 Non-Fan Industry Computer
  CPU: Intel® 1037U Dual-core 22nm Processor 1.8GHz TDP 17W
  Memory: Integrated DDR3 4GB Memory inboard
  Storage: 32G SSD
  LAN: 2* Intel 82583V 10/100/1000Mbps Ethernet,
  Dimension: 193 × 157 × 54mm
  Operating Temp.：0℃～55℃
  WLAN: WIFI or 3G
  I/O: 4 × USB2.0, 6 × COM, COM2 supports RS485, others support RS232
6xCOM

## Slide 5: Supervisory Controller Software

## Slide 6: Road Map
Protocols:
  BACnet MQTT Gateway
  BACnet Server (as data provider to 3rd party)
APPs:
  Kiosk in Lobby
  Wall Mount Tablet
  Android APP
  iOS APP
Hardware:
  Programmable Field Controllers
  Third Party AHUs
  Sensors: CO2, VOC, Formaldehyde, Temperature, Humidity, Pressure and Wind Speed